## Arc Flash
System Voltage (kV) | 0.48
Bolted Fault (kA) | 15
Arcing Time (s) | 0.1
Gap (mm) | 25
Working Distance (mm) | 455
Equipment | LV Switchgear
Arc Current (kA) | 9.8
Incident Energy (cal/cm²) | 4.2
Arc Flash Boundary (mm) | 1050
HRC | HRC 2
PPE | Arc-rated 8 cal/cm² + face shield

## Reference Data
Standard | IEEE 1584-2018
NFPA 70E